|  | REGULATORY REFORM (FIRE SAFETY) ORDER 2005 FIRE RISK ASSESSMENT |  |
| --- | --- | --- |
|  | Address of premises: Tel: Poole House – Facilities Block Fern Barrow Poole Dorset 01202 961626 Responsible person (e.g. employer) or person having control of the premises: Vice Chancellor, Bournemouth University Person(s) consulted: Tony Swan, Technical Services Manager Assessor: Stuart Jeneson, Fire Safety Officer, Bournemouth University Date of fire risk assessment: 3rd August 2017 Reviewed 31st October 2017 Date of previous fire risk assessment/audit 15 June 2015 Suggested date for review1): Oct 2019 |  |
|  | The purpose of this report is to provide an assessment of the risk to life from fire in these premises, and, where appropriate, to make recommendations to ensure compliance with fire safety legislation. The report does not address the risk to property or business continuity from fire. |  |
|  | 1) This fire risk assessment should be reviewed by a competent person by the date indicated above or at such earlier time as there is reason to suspect that it is no longer valid, or if there has been a significant change in the matters to which it relates, or if a fire occurs. |  |

|  | GENERAL INFORMATION |  |
| --- | --- | --- |
|  | 1. THE PREMISES Educational Establishment 1.1 Number of floors: Building six floors 1.2 Approximate site area: 3267 m² gross 1.3 Brief details of construction: Poole House is a large range of interconnected buildings of varying heights. Due to the size and compartmentation it has been nominally divided into 3 sections, Poole House Main Block, Sports Block and Facilities block. This risk assessment only focuses on the Facilities Block with the dividing line being the link corridor between the Sports Block and the Facilities Block along with the Atrium area of the Main Block. This section of Poole house is mainly ground floor only with 2 separate smaller areas where first floor accommodation is provided for offices and staff rooms. The building is constructed of steel and brick primarily and has had extensive modifications recently (2017). 1.4 Use of premises: This part of Poole house has mixed use. The largest space is devoted to a staff centre with supporting kitchen. The bulk of the remaining space is used as teaching and office accommodation. A number of higher risk activities take place including in the teaching area including an engineering workshop, wood machine workshop, plastic’s lab and paint spray room. There is also a general maintenance workshop and rooms devoted to food preparation in the form of an academic kitchen/food laboratory. 2. THE OCCUPANTS 2.1 Approximate maximum number: 400 2.2 Approximate number of employees at any one time: 50 2.3 Maximum number of members of public at any one time: 50 however varies 3. OCCUPANTS ESPECIALLY AT RISK FROM FIRE 3.1 Sleeping occupants: 0 3.2 Disabled occupants: Varies 3.3 Occupants in remote areas and lone workers: 0 3.4 Young persons: Varies 3.5 Others: 0 4. FIRE LOSS EXPERIENCE None recorded 5. OTHER RELEVANT INFORMATION The building has a full fire alarm system comprising automatic detection and manual call points generally appearing to conform to British Standard 5839 Part 1 Category L3. However it was noted that this level has been enhanced through most parts of the block to L2 standard. Fire alarm call points are sited throughout and at every storey exit. All installation certificates available. Emergency lighting has been installed conforming to BS 5266 Pt 1-1999 and consists of maintained and non-maintained units. P50 electrically safe foam fire extinguishers have been sited throughout all floors in strategic positions these replace both traditional water and CO2 extinguishers. 6. RELEVANT FIRE SAFETY LEGISLATION 6.1 The following fire safety legislation applies to these premises: The Regulatory Reform (Fire Safety) Order 2005 6.2 The above legislation is enforced by: Dorset and Wiltshire Fire & Rescue Service 6.3 Other legislation that makes significant requirements for fire precautions in these premises (other than the Building Regulations 2010): 6.4 The legislation to which 6.3 makes reference is enforced by: 6.5 Comments: |  |

|  | FIRE HAZARDS AND THEIR ELIMINATION OR CONTROL |  |
| --- | --- | --- |
|  | 7. ELECTRICAL SOURCES OF IGNITION 7.1 Reasonable measures taken to prevent fires of electrical origin? N/A Yes X No 7.2 More specifically: Fixed installation periodically inspected and tested? N/A Yes X No Portable appliance testing carried out? N/A N/A Yes X No Suitable policy regarding the use of personal electrical appliances? N/A Yes X No Suitable limitation of trailing leads and adapters? N/A Yes X No 7.3 Comments and hazards observed: New build test certificates available. Portable Appliance Testing – new equipment, procedures in place to grade appliances under a RAG system to allow for a risk assessed approach to PAT testing. 8. SMOKING 8.1 Reasonable measures taken to prevent fires as a result of smoking? N/A Yes X No 8.2 More specifically: Smoking prohibited in the building? N/A Yes X No Smoking prohibited in appropriate areas? N/A Yes X No Suitable arrangements for those who wish to smoke? N/A Yes X No This policy appeared to be observed at time of inspection? N/A Yes X No 8.3 Comments and hazards observed: University policy details that smoking only allowed 5 metres from the building this appears to be generally adhered to. Situation appears to be satisfactory. |  |

|  | 9. ARSON 9.1 Does basic security against arson by outsiders appear reasonable? 2) Yes X No 9.2 Is there an absence of unnecessary fire load in close proximity to the premises or available for ignition by outsiders? Yes X No 9.3 Comments and hazards observed: During the inspection some additional combustible storage was noted due to the move from Tolpuddle House (on Talbot Campus). However this was kept to a minimum and actively managed to control any risks. 10. PORTABLE HEATERS AND HEATING INSTALLATIONS 10.1 Is the use of portable heaters avoided as far as practicable? N/A Yes X No 10.2 If portable heaters are used: Is the use of the more hazardous type (e.g. radiant bar fires or lpg appliances) avoided? N/A Yes X No Are suitable measures taken to minimize the hazard of ignition of combustible materials? N/A Yes X No 10.3 Type of fixed heating installation: Gas boiler central heating with fixed radiators. 10.4 Are fixed heating installations subject to regular maintenance? N/A Yes X No 10.5 Comments and hazards observed: Gas fired heating –boilers in plant room with an additional Biomass boiler in a separated building - installation certificates available. No portable heaters witnessed during the inspection. Policy of the university does not allow the more hazardous heaters such as bar or halogen heaters. |  |
| --- | --- | --- |
|  | 2) Reasonable only in the context of this fire risk assessment. If specific advice on security (including security against arson) is required, the advice of a security specialist should be obtained. |  |

|  | 11. KITCHEN/COOKING 11.1 Are reasonable measures taken to prevent fires as a result of cooking? N/A Yes X No 11.2 More specifically: Filters changed and ductwork cleaned regularly? N/A Yes X No Suitable extinguishing appliances available? N/A Yes X No 11.3 Comments and hazards observed: There is no deep fat frying in this part of Poole House and ductwork is cleaned regularly as part of scheduled planned preventative maintenance. 12. LIGHTNING 12.1 Does the building have a lightning protection system? N/A Yes X No 12.2 Comments and deficiencies observed: Installation certificate available. Lightning protection will be tested by outside contactor every 11 months. Last inspection date 08/03/17 13. HOUSEKEEPING 13.1 Is the standard of housekeeping adequate? Yes X No 13.2 More specifically: Combustible materials appear to be separated from ignition sources? Yes X No Avoidance of unnecessary accumulation of combustible materials or waste? Yes X No Appropriate storage of hazardous materials? N/A X Yes No Avoidance of inappropriate storage of combustible materials? Yes X No 13.3 Comments and hazards observed: The inspection was carried out during the moving in period for the new Facilities block. As a consequence a number of corridors and rooms had unnecessary storage however this was being dealt with as and when required. In general the standard is satisfactory. |  |
| --- | --- | --- |

|  | 14. HAZARDS INTRODUCED BY OUTSIDE CONTRACTORS AND BUILDING WORKS 14.1 Are fire safety conditions imposed on outside contractors? N/A Yes X No 14.2 Is there satisfactory control over works carried out in the building by outside contractors (including “hot work” permits)? N/A Yes X No 14.3 If there are in-house maintenance personnel, are suitable precautions taken during “hot work”, including use of hot work permits? N/A Yes X No 14.4 Comments: Contractors are provided with documentation regarding all Health and Safety issues including fire when contracted to do work for the university- this includes an induction PowerPoint presentation Hot Works Permits are provided when required by management. 15. DANGEROUS SUBSTANCES 15.1 If dangerous substances are, or could be, used, has a risk assessment been carried out, as required by the Dangerous Substances and Explosive Atmospheres Regulations 2002? N/A Yes X No 15.2 Comments: A number of areas contain small amounts of flammable liquids – these are tightly controlled and quantities both in use and stored kept to the minimum necessary. At present 2 size W Argon and Argosheild lite and 1 CO2 size VK and held in the engineering workshop (PG89) in the welding bay area. Although these are non-flammable no signage has been displayed indicating their use – see action plan. A further assessment of the suitability of the area should be made with regard to ventilation and structural protection offered in the area chosen by the design team. – see action plan 16. OTHER SIGNIFICANT FIRE HAZARDS THAT WARRANT CONSIDERATION INCLUDING PROCESS HAZARDS THAT IMPACT ON GENERAL FIRE PRECAUTIONS 16.1 Hazards: A number of higher risk activities take place within the various workshops including, Welding, 3D printing with melted plastics, wood working and paint spraying - however these are strictly monitored with no student being allowed to work unsupervised. 16.2 Comments and deficiencies observed: |  |
| --- | --- | --- |

|  | FIRE PROTECTION MEASURES |  |
| --- | --- | --- |
|  | 17. MEANS OF ESCAPE FROM FIRE 17.1 It is considered that the site is provided with reasonable means of escape in case of fire. Yes No X 17.2 More specifically: N/A Adequate design of escape routes? Yes X No Adequate provision of exits? Yes X No Exits easily and immediately openable where necessary? Yes X No Fire exits open in direction of escape where necessary? Yes X No Avoidance of sliding or revolving doors as fire exits where necessary? Yes X No Satisfactory means for securing exits? Yes X No Reasonable distances of travel: • Where there is a single direction of travel? Yes X No • Where there are alternative means of escape? N/A Yes X No Suitable protection of escape routes? Yes No X Including doors, screens, and walls. Suitable fire precautions for all inner rooms? N/A Yes X No Escape routes unobstructed? Yes X No 17.3 It is considered that the building is provided with reasonable arrangements for means of escape for disabled people. N/A Yes X No 17.4 Comments and deficiencies observed: Extensive building modifications have taken place and the MOE appears generally satisfactory – however the protection to corridor PGC37 from the staff centre requires reviewing - See Action Plan reference door and structure issues. |  |

|  | 18. MEASURES TO LIMIT FIRE SPREAD AND DEVELOPMENT 18.1 It is considered that there is: compartmentation of a reasonable standard3). Yes No X reasonable limitation of linings that might promote fire spread. Yes X No 18.2 As far as can reasonably be ascertained, fire dampers are provided as necessary to protect critical means of escape against passage of fire, smoke and combustion products in the early stages of a fire? 3), 4) N/A Yes X No 18.3 Comments and deficiencies observed: In parts of the Facilities block compartmentation issues have been addressed however there are a number of areas where fire lines are breached and/or ineffective. Independent accredited contractor should be employed to ensure compliance and best practice regarding compartmentation – see action plan A number of fire doors were wedged open at the time of inspection due to office moves this was raised and assurances given by staff that wedges would be managed if a fire alarm were to activate. 19. EMERGENCY ESCAPE LIGHTING 19.1 Reasonable standard of emergency escape lighting system provided? 5) N/A Yes X No 19.2 Comments and deficiencies observed: Self-contained battery luminaires, some maintained, appearing to conform to British Standard 5266: Part 1. 20. FIRE SAFETY SIGNS AND NOTICES 20.1 Reasonable standard of fire safety signs and notices? Yes X No 20.2 Comments and deficiencies observed: Refuges are provided with identification signs, all call points have fire action notices nearby. An appropriate standard is being maintained. |  |
| --- | --- | --- |
|  | 3) Based on visual inspection of readily accessible areas, with a degree of sampling where appropriate. 4) A full investigation of the design of HVAC systems is outside the scope of this fire risk assessment. 5) Based on visual inspection, but no test of illuminance levels or verification of full compliance with relevant British Standards carried out. |  |

|  | 21. MEANS OF GIVING WARNING IN CASE OF FIRE 21.1 Reasonable manually operated electrical fire alarm system provided? 6) Yes X No 21.2 Automatic fire detection provided? Yes Yes X No (throughout building) (part of building only) 21.3 Extent of automatic fire detection generally appropriate for the occupancy and fire risk? N/A Yes X No 21.4 Remote transmission of alarm signals? N/A Yes No X 21.5 Satisfactory policy N/A X Yes No In accordance with CFOA Policy ‘Model Agreement for Remotely Monitored Fire Alarm Systems’ 21.6 Comments and deficiencies observed: The building has a full fire alarm system comprising automatic detection and manual call points generally appearing to conform to British Standard 5839 Part 1 Category L3. However it was noted that this level has been enhanced through some parts of the block to L2 standard. Fire alarm call points are sited throughout and at every storey exit. 22. MANUAL FIRE EXTINGUISHING APPLIANCES 22.1 Reasonable provision of portable fire extinguishers? Yes X No 22.2 Hose reels provided? Yes No X 22.3 Are all fire extinguishing appliances readily accessible? N/A Yes X No 22.4 Comments and deficiencies observed: Fire extinguishers provided complying with the guidance of BS5306-8:2012 part 8, it should be noted that the annual service of Britannia P50 foam extinguishers is completed in house as detailed in manufacturer’s instructions. |  |
| --- | --- | --- |
|  | 6) Based on visual inspection, but no audibility tests or verification of full compliance with relevant British Standard carried out. |  |

|  | 23. RELEVANT7) AUTOMATIC FIRE EXTIGUISHING SYSTEMS 23.1 Type of system: None 23.2 Comments: 24. OTHER RELEVANT 7) FIXED SYSTEMS AND EQUIPMENT 24.1 Type of fixed system: 24.2 Comments: None 24.3 Suitable provision of fire-fighters switch(es) for high voltage luminous tube signs, etc. N/A X Yes No 24.4 Comments: None |  |
| --- | --- | --- |
|  | 7) Relevant to life safety and this risk assessment (as opposed purely to property protection). |  |

|  | MANAGEMENT OF FIRE SAFETY |  |
| --- | --- | --- |
|  | 25. PROCEDURES AND ARRANGEMENTS 25.1 Fire safety is managed by: 8) S. Laird , Director of Estates 25.2 Competent person(s) appointed to assist in undertaking the preventive and protective measures (i.e. relevant general fire precautions)? Yes X No Comments: Stu Jeneson, Fire Officer, Bournemouth University for fire risk assessment In house staff service and maintain emergency lighting system Wessex Electrical appointed to service and maintain fire alarm system In house staff service and maintain portable fire-fighting equipment (10 year maintenance free) 25.3 Is there a suitable record of the fire safety arrangements? N/A Yes X No Comments: An overarching fire policy and management document is in place along with numerous operational documents. 25.4 Appropriate fire procedures in place? Yes X No More specifically: Are procedures in the event of fire appropriate and properly documented? N/A Yes X No Are there suitable arrangements for summoning the fire and rescue service? Yes X No Are there suitable arrangements to meet the fire and rescue service on arrival and provide relevant information, including that relating to hazards to fire-fighters? N/A Yes X No Are there suitable arrangements for ensuring that the premises have been evacuated? N/A Yes X No Is there a suitable fire assembly point(s)? N/A Yes X No Are there adequate procedures for evacuation of any disabled people who are likely to be present? N/A Yes X No |  |
|  | 8) This is not intended to represent a legal interpretation of responsibility, but merely reflects the managerial arrangement in place at the time of this risk assessment. |  |

|  | Comments: Procedure documentation available and suitable, all emergency calls are sent via the reception within Poole House. The building has a premises information box that contains all information required by the fire service along with procedures to be followed by the Fire Marshal. Assembly points are provided and used during practice evacuations. PEEPS are provided for disabled people as required along with refuges with communication points linked back to the fire panel area. 25.5 Persons nominated and trained to use fire extinguishing appliances? N/A Yes X No Comments: Fire Wardens are given initial training and refresher training is provided every three years this includes fire extinguisher usage (not practical). It is the policy of BU there is no expectation or requirement to use extinguishers unless the individual is competent and confident to do so. 25.6 Persons nominated and trained to assist with evacuation, including evacuation of disabled people? N/A Yes X No Comments: Evacuation chairs are provided in the building and specific estate staff are trained in the evacuation of disabled individuals. 25.7 Appropriate liaison with fire and rescue service (e.g. by fire and rescue service crews visiting for familiarization visits)? N/A Yes X No Comments: The Fire Officer maintains good contact with Operational and fire safety staff in Dorset and Wiltshire Fire and Rescue. 25.8 Routine in-house inspections of fire precautions (e.g. in the course of health and safety inspections)? N/A Yes X No Comments: None |  |
| --- | --- | --- |

|  | 26. TRAINING AND DRILLS 26.1 Are all staff given adequate fire safety instruction and training on induction? N/A Yes X No Comments: The responsibility for initial fire induction training is individuals line managers; additionally a bespoke fire safety on line package is used throughout the University, it is a requirement that new employees complete the module as soon as possible after they have started. Individual Faculties are responsible for providing site specific instruction to their staff regarding responsibilities for evacuation of students. 26.2 Are all staff given adequate periodic “refresher training” at suitable intervals? N/A Yes No X Comments: The online training detailed above is completed annually by staff. 26.3 Does all staff training provide information, instruction or training on the following: N/A Fire risks in the premises? Yes X No The fire safety measures in the building? Yes X No Action in the event of fire? Yes X No Action on hearing the fire alarm signal? Yes X No Method of operation of manual call points? Yes X No Location and use of fire extinguishers? Yes X No Means for summoning the fire and rescue service? Yes X No Identity of persons nominated to assist with evacuation? N/A Yes X No Procedures for the safe evacuation of all occupants? Yes X No Comments: |  |
| --- | --- | --- |

|  | 26.4 Are staff with special responsibilities (e.g. fire wardens) given additional training? N/A Yes X No Comments: Fire Wardens are given initial training and refresher training is provided every three years this includes fire extinguisher training. Additional Fire Wardens should be identified to ensure a complete evacuation sweep is achievable on all floors. 26.5 Are fire drills carried out at appropriate intervals? N/A Yes X No Comments: Fire drills carried out annually and details recorded. Additional evacuations occur throughout the year due to false alarms – these again are recorded to identify causes. 26.6 When the employees of another employer work in the premises: Is their employer given appropriate information (e.g. on fire risks and general fire precautions)? N/A Yes X No Is it ensured that the employees are provided with adequate instructions and information? N/A Yes X No Each member of staff Comments: Paperwork and induction process for external employees on arrival at the Estates Office. 27. TESTING AND MAINTENANCE 27.1 Adequate maintenance of premises? N/A Yes No X Comments and deficiencies observed: Refer to comments below 27.2 Weekly testing and periodic servicing of fire detection and alarm system? N/A Yes X No Comments and deficiencies observed: Monthly tests are carried out – this departure from BS5839 has been fully risk assessed and agreed with the Fire Service. System serviced in accordance with BS5839 Pt 1 Installation certificates confirming compliance available. 27.3 Monthly and annual testing routines for emergency escape lighting? N/A Yes X No Comments and deficiencies observed: Monthly test carried out System serviced in accordance with BS5266 Pt 1 Installation certificates confirming compliance available. 27.4 Routine inspection and annual maintenance of fire extinguishers. N/A Yes X No Comments and deficiencies observed: New Britannia P50 6 litre foam extinguisher installed throughout premises – these are maintenance free for 10 years however regular checks are carried out to ensure they remain serviceable / available. 27.5 Periodic inspection of external escape staircases, paths and gangways? N/A X Yes No Comments and deficiencies observed: None 27.6 Six-monthly inspection and annual testing of rising mains? N/A X Yes No Comments and deficiencies observed: Dry Riser in the Main Block section of Poole House 27.7 Weekly and monthly testing, six monthly inspection and annual testing of fire-fighting lifts? N/A X Yes No Comments and deficiencies observed: 27.8 Weekly testing and periodic inspection of sprinkler installations? N/A X Yes No Comments: None fitted in this section of Poole House |  |
| --- | --- | --- |

|  | 27.9 Routine checks of final exit doors and/or security fastenings? N/A Yes No X Comments: This is not completed – procedures should be adopted. 27.10 Annual inspection and test of lightning protection system? N/A Yes X No Comments: This is completed by an external contractor. None 27.11 Routine inspection and testing of fire resisting doors? N/A Yes No X Comments: This currently is not carried out – see action plan √ 27.12 Other relevant inspections or tests: None Comments: 28. RECORDS 28.1 Appropriate records of: Fire drills? N/A Yes X No Fire training? N/A Yes X No Fire alarm tests? N/A Yes X No Emergency escape lighting tests? N/A Yes X No Maintenance and testing of other fire protection systems/provisions including sprinklers, portable fire fighting equipment, fire doors and exit doors. N/A Yes No X 28.2 Comments: Records are being maintained – see action plan regarding fire doors and exit doors. |  |
| --- | --- | --- |

|  | FIRE RISK ASSESSMENT |  |
| --- | --- | --- |
|  | The following simple risk level estimator is based on a more general health and safety risk level estimator of the type contained in BS 8800: Potential consequences of fire Likelihood of fire Slight harm Moderate harm Extreme harm Low Trivial risk Tolerable risk Moderate risk Medium Tolerable risk Moderate risk Substantial risk High Moderate risk Substantial risk Intolerable risk Taking into account the fire prevention measures observed at the time of this risk assessment, it is considered that the hazard from fire (likelihood of fire) at these premises is: Low Medium X High In this context, a definition of the above terms is as follows: Low: Unusually low likelihood of fire as a result of negligible potential sources of ignition. Medium: Normal fire hazards (e.g. potential ignition sources) for this type of occupancy, with fire hazards generally subject to appropriate controls (other than minor shortcomings). High: Lack of adequate controls applied to one or more significant fire hazards, such as to result in significant increase in likelihood of fire. Taking into account the nature of the building and the occupants, as well as the fire protection and procedural arrangements observed at the time of this fire risk assessment, it is considered that the consequences for life safety in the event of fire would be: Slight harm X X Moderate harm X Extreme harm In this context, a definition of the above terms is as follows: Slight harm: Outbreak of fire unlikely to result in serious injury or death of any occupant (other than an occupant sleeping in a room in which a fire occurs). Moderate harm: Outbreak of fire could foreseeably result in injury (including serious injury) of one or more occupants, but it is unlikely to involve multiple fatalities. Extreme harm: Significant potential for serious injury or death of one or more occupants. |  |

|  | Accordingly, it is considered that the risk to life from fire at these premises is: Trivial Tolerable X Moderate Substantial Intolerable Comments: None A suitable risk-based control plan should involve effort and urgency that is proportional to risk. The following risk-based control plan is based on one advocated by BS 8800 for general health and safety risks: Risk level Action and timescale Trivial No action is required and no detailed records need be kept. Tolerable No major additional controls required. However, there might be a need for improvements that involve minor or limited cost. Moderate It is essential that efforts are made to reduce the risk. Risk reduction measures should be implemented within a defined time period. Where moderate risk is associated with consequences that constitute extreme harm, further assessment might be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures. Substantial Considerable resources might have to be allocated to reduce the risk. If the building is unoccupied, it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken. Intolerable Building (or relevant area) should not be occupied until the risk is reduced. (Note that, although the purpose of this section is to place the fire risk in context, the above approach to fire risk assessment is subjective and for guidance only. All hazards and deficiencies identified in this report should be addressed by implementing all recommendations contained in the following action plan. The fire risk assessment should be reviewed regularly.) |  |
| --- | --- | --- |
|  | ACTION PLAN |  |
|  | It is considered that the following recommendations should be implemented in order to reduce fire risk to, or maintain it at, the following level: Trivial Tolerable X Definition of priorities (where applicable): Urgent – To be completed as soon as reasonably practicable usually within a week. Priority 1 – To be completed within 1 – 4 weeks Priority 2 – To be completed within 1 – 3 months Priority 3 – To be completed within 4 – 8 months No priority It is considered that the following recommendations should be implemented in order to reduce fire risk to, or maintain it at, the following level: Trivial Tolerable X Priority (where applicable) Action by whom Date action taken Fire Doors should be regularly checked – it is recommended a procedure is adopted to ensure all doors are checked annually. 2 R. White, Hard Services Manager Recommendation for a full compartmentation survey of Poole House 2 R. White, Hard Services Manager The following points require attention PG71 Doors Opp PG 60 Sports – smoke seal missing and adjust to close PG71 Opp end of corridor – minor adjustment to close properly PGT21 Minor adjustment to close properly PG71 Single fire door near food counter – review door in poor condition PG71 Double Fire Exit door to Potwash area – sticking on carpet – no I/S or smoke seals – excessive central gap PG71 Potwash area from double doors – directional exit sign required on wall (pointing left) Opposite PG83 Self-closing automatic doors damaged at low level – IS strip loose and parts of door missing PGC30 Door to estates office – Smoke seal missing top and side PGL38 Doors to lobby before final exit – I/S strip missing Opposite PG 85 Self-closing automatic doors minor adjustment to close properly 1 R. White, Hard Services Manager Work orders Engineering Workshop PG89 At present 2 size W Argon and Argosheild lite and 1 CO2 size VK and held in the engineering workshop (PG89) in the welding bay area. Although these are non-flammable no signage has been displayed indicating their use. A further assessment of the suitability of the area should be made with regard to ventilation and structural protection offered in the area chosen for the welding bay along with the floor covering (plastic/rubberized tiles). 1 Russell Evans Completed 15/08/17 The inspection of all external routes and final exit doors is not formally recorded and should be addressed. 3 S. Baylis Soft Services Manager |  |

# Text boxes

1

2

3