|  |  |  |
| --- | --- | --- |
|  | 1. **REGULATORY REFORM (FIRE SAFETY) ORDER 2005**
2. **FIRE RISK ASSESSMENT**
 |  |
|  |

|  |  |
| --- | --- |
| 1. Address of premises:

Tel:  | 1. ***Unit 5***
2. ***Drewitt Industrial Estate***
3. ***865 Ringwood Road***
4. ***Bournemouth***
5. ***BH11 8LL***
6. ***01202 961626 (Poole House)***
 |
| 1. Responsible person (e.g. employer) or person having control of the premises:
 | 1. ***Vice Chancellor, Bournemouth University***
 |
| 1. Person(s) consulted:
 | 1. ***Tony Swan, Technical Services Manager***
 |
| 1. Assessor:
 | 1. ***David Gale Tech IOSH , Fire Safety Officer, Bournemouth University***
 |
| 1. Date of fire risk assessment:
 | 1. ***16 April 2019***
 |
| 1. Date of previous fire risk assessment/audit
 | 1. ***28 March 2018***
 |
| 1. Suggested date for review1):
 | 1. ***April 2022***
 |

 |  |
|  |  |  |
|  | The purpose of this report is to provide an assessment of the risk to life from fire in these premises, and, where appropriate, to make recommendations to ensure compliance with fire safety legislation. The report does not address the risk to property or business continuity from fire. |  |
|  |  |  |
|  |  |  |  |
|  | 1. 1) This fire risk assessment should be reviewed by a competent person by the date indicated above or at such earlier time as there is reason to suspect that it is no longer valid, or if there has been a significant change in the matters to which it relates, or if a fire occurs.
 |  |
|  |  |  |

|  |  |  |
| --- | --- | --- |
|  | 1. **GENERAL INFORMATION**
 |  |
|  |

|  |  |
| --- | --- |
| 1. **1.**
 | 1. **THE PREMISES Storage Unit**
 |
| 1. 1.1
 | 1. Number of floors ***Single Storey***
2.
 |
| 1. 1.2
 | 1. Approximate site area:
 | 1. ***180m² gross***
 |
|  |  | 1.
 |
|  |  | 1.
 |
|  |  |  |
| 1. 1.3
 | 1. Brief details of construction:
2. ***The building is traditionally constructed of steel and brick with a composite steel roof. Internally small rooms are provided at the rear for office space – these have glazing allowing full visibility into the main area – also toilets and a small kitchen area are located by the front entrance. A full roller shutter is provided along with a conventional front door allowing access to the unit.***
 |
| 1. 1.4
 | 1. Use of premises: ***The building is a storage unit currently unoccupied and empty. Its intended use is for storage of items of furniture – staff will be in attendance to drop off and/or pick up items for a short period only.***
 |
| 1. **2.**
 | 1. **THE OCCUPANTS**
 |
| 1. 2.1
 | 1. Approximate maximum number:
 | 1. ***4***
 |
| 1. 2.2
 | 1. Approximate number of employees at any one time:
2.
 | 1. ***2 – occasional use only***
 |
| 1. 2.3
 | 1. Maximum number of members of public at any one time:
 | 1. ***0***
 |
| 1. **3.**
 | **OCCUPANTS ESPECIALLY AT RISK FROM FIRE** |
| 1. 3.1
 | 1. Sleeping occupants:
2.
 | 1. ***0***
 |
| 1. 3.2
 | 1. Disabled occupants:
 | 1. ***0***
 |
| 1. 3.3
 | 1. Occupants in remote areas and lone workers:
 | 1. ***0***
 |
| 1. 3.4
 | 1. Young persons:
 | 1. ***0***
 |
| 1. 3.5
 | 1. Others:
 | 1. ***0***
 |
|  |

|  |  |
| --- | --- |
| 1. **4.**
 | 1. **FIRE LOSS EXPERIENCE**
 |
|  | 1. ***None recorded***
 |
| 1. **5.**
 | 1. **OTHER RELEVANT INFORMATION**
 |
|  | 1. ***Means of Escape***
2. ***The evacuation strategy on detection of a fire is that all occupants will simultaneously evacuate to a place of safety outside the building.***
3. ***A rear exit does gives access to an enclosed yard – this is not considered to be suitable as a means of escape as there is no exit from this yard.***
 |

 |  |
|  |

|  |  |
| --- | --- |
| 1. **6.**
 | 1. **RELEVANT FIRE SAFETY LEGISLATION**
 |
| 1. 6.1
 | 1. The following fire safety legislation applies to these premises:
 |
|  | 1. ***The Regulatory Reform (Fire Safety) Order 2005***
 |
| 1. 6.2
 | 1. The above legislation is enforced by:
 |
|  | 1. ***Dorset and Wiltshire Fire & Rescue Service***
 |
| 1. 6.3
 | 1. Other legislation that makes significant requirements for fire precautions in these premises (other than the Building Regulations 2010):
 |
|  |  |
| 1. 6.4
 | 1. The legislation to which 6.3 makes reference is enforced by:
 |
|  |  |
| 1. 6.5
 | 1. Comments:
 |
|  |  |

 |  |
|  |  |  |

 |  |

|  |  |  |
| --- | --- | --- |
|  | 1. **FIRE HAZARDS AND THEIR ELIMINATION OR CONTROL**
 |  |
|  |

|  |  |
| --- | --- |
| 1. **7.**
 | 1. **ELECTRICAL SOURCES OF IGNITION**
 |
| 1. 7.1
 | 1. Reasonable measures taken to prevent fires of electrical origin?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 7.2
 | 1. More specifically:
 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Fixed installation periodically inspected and tested?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Portable appliance testing carried out?
 | 1. N/A N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Suitable policy regarding the use of personal electrical appliances?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Suitable limitation of trailing leads and adapters?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |  |
| 1. 7.3
 | 1. Comments and hazards observed:
 |  |  |  |  |  |  |
|  | 1. ***Fixed installation last inspection May 2015 – next due May 2020***
 |
| 1. **8.**
 | 1. **SMOKING**
 |
| 1. 8.1
 | 1. Reasonable measures taken to prevent fires as a result of smoking?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 8.2
 | 1. More specifically:
 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Smoking prohibited in the building?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Smoking prohibited in appropriate areas?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Suitable arrangements for those who wish to smoke?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. This policy appeared to be observed at time of inspection?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 8.3
 | 1. Comments and hazards observed:
 |  |  |  |  |  |  |
|  | 1. ***Situation satisfactory.***
 |

 |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |
| --- | --- |
| 1. **9.**
 | 1. **ARSON**
 |
| 1. 9.1
 | 1. Does basic security against arson by outsiders appear reasonable? 2)
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 9.2
 | 1. Is there an absence of unnecessary fire load in close proximity to the premises or available for ignition by outsiders?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 9.3
 | 1. Comments and hazards observed:
 |  |  |  |  |  |  |
|  |  |
| 1. **10.**
 | 1. **PORTABLE HEATERS AND HEATING INSTALLATIONS**
 |
| 1. 10.1
 | 1. Is the use of portable heaters avoided as far as practicable?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 10.2
 | 1. If portable heaters are used:
 |  |  |  |  |  |  |
|  | 1. Is the use of the more hazardous type (e.g. radiant bar fires or lpg appliances) avoided?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Are suitable measures taken to minimize the hazard of ignition of combustible materials?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
| 1. 10.3
 | 1. Type of fixed heating installation:
2. ***Gas fired warm air heating fixed to the ceiling .***
 |  |  |  |  |  |  |
| 1. 10.4
 | 1. Are fixed heating installations subject to regular maintenance?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 10.5
 | 1. Comments and hazards observed:
 |  |  |  |  |  |  |
|  | 1. ***Gas heating – serviced 23/01/19 - records available***
2. ***Area around heater must be kept clear of stacked goods on occupation. Consideration should be given to isolating the heater as the unit will be used for storage of furniture items only.***
 |

 |  |
|  |  |  |  |
|  | 1. 2) Reasonable only in the context of this fire risk assessment. If specific advice on security (including security against arson) is required, the advice of a security specialist should be obtained.
 |  |
|  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |
| --- | --- |
| 1. **11.**
 | 1. **KITCHEN/COOKING**
 |
| 1. 11.1
 | 1. Are reasonable measures taken to prevent fires as a result of cooking?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 11.2
 | 1. More specifically:
 |  |  |  |  |  |  |
|  | 1. Filters changed and ductwork cleaned regularly?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Suitable extinguishing appliances available?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |  |
| 1. 11.3
 | 1. Comments and hazards observed:
 |
|  | 1. ***Kitchenette unused at time of inspection – no plans to use this facility on occupation – currently no extinguishers provided.***
2.
 |
| 1. **12.**
 | 1. **LIGHTNING**
 |
| 1. 12.1
 | 1. Does the building have a lightning protection system?
 | 1. N/A
 |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  |  |  |  |  |  |  |  |
| 1. 12.2
 | 1. Comments and deficiencies observed:
 |
|  | 1.
 |
| 1. **13.**
 | 1. **HOUSEKEEPING**
 |
| 1. 13.1
 | 1. Is the standard of housekeeping adequate?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
| 1. 13.2
 | More specifically: |  |  |  |  |  |  |
|  |  Combustible materials appear to be separated from ignition sources? |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  Avoidance of unnecessary accumulation of combustible materials or waste? |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  Appropriate storage of hazardous materials? | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  |  Avoidance of inappropriate storage of combustible materials? |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 13.3
 | 1. Comments and hazards observed:
 |
|  | 1. ***At the time of the inspection the unit was being used for storage.***
2. ***Due to poor housekeeping the storage was too close to the electrical intake and blocking the fire exit route***
 |

 |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |
| --- | --- |
| 1. **14.**
 | 1. **HAZARDS INTRODUCED BY OUTSIDE CONTRACTORS AND BUILDING WORKS**
 |
| 1. 14.1
 | 1. Are fire safety conditions imposed on outside contractors?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |  |
| 1. 14.2
 | 1. Is there satisfactory control over works carried out in the building by outside contractors (including “hot work” permits)?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 14.3
 | 1. If there are in‑house maintenance personnel, are suitable precautions taken during “hot work”, including use of hot work permits?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 14.4
 | 1. Comments:
 |
|  | 1. ***Any contractors tasked to work within any BU premise are provided with documentation regarding all Health and Safety issues including fire when contracted to do work for the university.***
 |
| 1. **15.**
 | 1. **DANGEROUS SUBSTANCES**
 |
| 1. 15.1
 | 1. If dangerous substances are, or could be, used, has a risk assessment been carried out, as required by the Dangerous Substances and Explosive Atmospheres Regulations 2002?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 15.2
 | 1. Comments:
 |
|  |  |
| 1. **16.**
 | 1. **OTHER SIGNIFICANT FIRE HAZARDS THAT WARRANT CONSIDERATION INCLUDING PROCESS HAZARDS THAT IMPACT ON GENERAL FIRE PRECAUTIONS**
 |
| 1. 16.1
 | 1. Hazards:
 |
|  | 1. ***None***
 |
| 1. 16.2
 | 1. Comments and deficiencies observed:
 |
|  |  |

 |  |
|  |  |  |

|  |  |  |
| --- | --- | --- |
|  | 1. **FIRE PROTECTION MEASURES**
 |  |
|  |

|  |  |
| --- | --- |
| 1. **17.**
 | 1. **MEANS OF ESCAPE FROM FIRE**
 |
| 1. 17.1
 | 1. It is considered that the site is provided with reasonable means of escape in case of fire.
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 17.2
 | 1. More specifically:
 | 1. N/A
 |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Adequate design of escape routes?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Adequate provision of exits?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Exits easily and immediately openable where necessary?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Fire exits open in direction of escape where necessary?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Avoidance of sliding or revolving doors as fire exits where necessary?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Satisfactory means for securing exits?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Reasonable distances of travel:
 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  |  • Where there is a single direction of travel? |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  |  • Where there are alternative means of escape? | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Suitable protection of escape routes?
 |  |  | 1. Yes
 |  | 1. No
 | 1. **N/A**
 |
|  | 1. Including doors, screens, and walls.
 |  |  |  |  |  |  |
|  | 1. Suitable fire precautions for all inner rooms?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Escape routes unobstructed?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
| 1. 17.3
 | 1. It is considered that the building is provided with reasonable arrangements for means of escape for disabled people.
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 17.4
 | 1. Comments and deficiencies observed:
 |  |  |  |  |  |  |
|  | 1. ***The main entrance door is always open and available when people are in the unit. as previously stated the rear exit discharges into an enclosed yard from which there is no route out, there is an alternative fire exit door to the side of the roller shutter door. As the use of the premises is for storage only and will only be occupied during the loading/unloading of furniture and therefore the large roller shutter door open - this is considered adequate as means of escape.***
 |

 |  |
|  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |
| --- | --- |
| 1. **18.**
 | 1. **MEASURES TO LIMIT FIRE SPREAD AND DEVELOPMENT**
 |
| 1. 18.1
 | 1. It is considered that there is:
 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. compartmentation of a reasonable standard3).
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. reasonable limitation of linings that might promote fire spread.
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 18.2
 | 1. As far as can reasonably be ascertained, fire dampers are provided as necessary to protect critical means of escape against passage of fire, smoke and combustion products in the early stages of a fire? 3), 4)
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 18.3
 | 1. Comments and deficiencies observed:
 |
|  |  |
| 1. **19.**
 | 1. **EMERGENCY ESCAPE LIGHTING**
 |
| 1. 19.1
 | 1. Reasonable standard of emergency escape lighting system provided? 5)
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 19.2
 | 1. Comments and deficiencies observed:
 |
|  | 1. ***Self-contained battery luminaires, some maintained, appearing to conform to British Standard 5266: Part 1.***
 |
| 1. **20.**
 | 1. **FIRE SAFETY SIGNS AND NOTICES**
 |
| 1. 20.1
 | 1. Reasonable standard of fire safety signs and notices?
 |  |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  |  |  |  |  |  |  |  |
| 1. 20.2
 | 1. Comments and deficiencies observed: ***Fire action notice required for the alternative fire exit* door**
 |
|  |  |

 |  |
|  |  |  |  |
|  | 1. 3) Based on visual inspection of readily accessible areas, with a degree of sampling where appropriate.
2. 4) A full investigation of the design of HVAC systems is outside the scope of this fire risk assessment.
3. 5) Based on visual inspection, but no test of illuminance levels or verification of full compliance with relevant British Standards carried out.
 |  |
|  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |
| --- | --- |
| 1. **21.**
 | 1. **MEANS OF GIVING WARNING IN CASE OF FIRE**
 |
| 1. 21.1
 | 1. Reasonable manually operated electrical fire alarm system provided? 6)
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 21.2
 | 1. Automatic fire detection provided?
 | 1. Yes
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  | 1. (throughout building)
 | 1. (part of building only)
 |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 21.3
 | 1. Extent of automatic fire detection generally appropriate for the occupancy and fire risk?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| 1. 21.4
 | 1. Remote transmission of alarm signals?
 | 1. N/A
 |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  |  |  |  |  |  |  |  |  |
| 1. 21.5
 | 1. Satisfactory policy
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  | In accordance with CFOA Policy ‘Model Agreement for Remotely Monitored Fire Alarm Systems’ |
| 21.6 | 1. Comments and deficiencies observed:
2. ***The building has a fire alarm system comprising of a manual call points, and automatic smoke detection.***
3. ***This is currently not linked to any ARC***
 |
| 1. **22.**
 | 1. **MANUAL FIRE EXTINGUISHING APPLIANCES**
 |
| 1. 22.1
 | 1. Reasonable provision of portable fire extinguishers?
 |  |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  |  |  |  |  |  |  |  |
| 1. 22.2
 | 1. Hose reels provided?
 |  |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  |  |  |  |  |  |  |  |
| 1. 22.3
 | 1. Are all fire extinguishing appliances readily accessible?
 | 1. N/A
 |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  |  |  |  |  |  |  |  |
| 1. 22.4
 | Comments and deficiencies observed:***Water fire extinguishers provided at time of inspection, these did not appear to the property of BU or being tested.******It is recommended that P50 foam extinguishers should be provided to BS 5306 - 8***  |

 |  |
|  |  |  |  |
|  | 1. 6) Based on visual inspection, but no audibility tests or verification of full compliance with relevant British Standard carried out.
 |  |
|  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |
| --- | --- |
| 1. **23.**
 | 1. **RELEVANT**7) **AUTOMATIC FIRE EXTIGUISHING SYSTEMS**
 |
| 1. 23.1
 | 1. Type of system:
 |
|  | 1. ***None***
 |
| 1. 23.2
 | 1. Comments:
 |
|  |  |
| 1. **24.**
 | 1. **OTHER RELEVANT** 7) **FIXED SYSTEMS AND EQUIPMENT**
 |
| 1. 24.1
 | 1. Type of fixed system:
 |
|  | 1. ***None***
 |
| 1. 24.2
 | 1. Comments:
 |
|  | 1. ***None***
2.
 |
| 1. 24.3
 | 1. Suitable provision of fire‑fighters switch(es) for high voltage luminous tube signs, etc.
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |
| 1. 24.4
 | 1. Comments:
 |
|  | 1. ***None***
 |

 |  |
|  |  |  |  |
|  | 1. 7) Relevant to life safety and this risk assessment (as opposed purely to property protection).
 |  |
|  |  |  |

|  |  |  |
| --- | --- | --- |
|  | 1. **MANAGEMENT OF FIRE SAFETY**
 |  |
|  |

|  |  |
| --- | --- |
| 1. **25.**
 | 1. **PROCEDURES AND ARRANGEMENTS**
 |
| 1. 25.1
 | 1. Fire safety is managed by: 8)
 |
|  | 1. ***S. Laird , Director of Estates***
 |
| 1. 25.2
 | 1. Competent person(s) appointed to assist in undertaking the preventive and protective measures (i.e. relevant general fire precautions)?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | 1. ***David Gale Tech IOSH, Fire Officer, Bournemouth University for fire risk assessment***
2. ***In house staff service and maintain emergency lighting system and fire extinguishers***
3. ***Wessex Fire appointed to service and maintain fire alarm system***
 |
| 1. 25.3
 | 1. Is there a suitable record of the fire safety arrangements?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | 1. ***An overarching fire policy and management document is in place along with numerous operational documents.***
 |
| 1. 25.4
 | 1. Appropriate fire procedures in place?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. More specifically:
 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Are procedures in the event of fire appropriate and properly documented?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Are there suitable arrangements for summoning the fire and rescue service?
 |  |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Are there suitable arrangements to meet the fire and rescue service on arrival and provide relevant information, including that relating to hazards to fire‑fighters?
 | 1. N/A
 |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Are there suitable arrangements for ensuring that the premises have been evacuated?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Is there a suitable fire assembly point(s)?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Are there adequate procedures for evacuation of any disabled people who are likely to be present?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |

 |  |
|  |  |  |  |
|  | 1. 8) This is not intended to represent a legal interpretation of responsibility, but merely reflects the managerial arrangement in place at the time of this risk assessment.
 |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |
| --- | --- |
|  | 1. Comments:
 |
|  | ***This storage unit is remote from other BU buildings and unoccupied.*** ***See comments in section 21.6 regarding summing the FRS*** |
| 1. 25.5
 | 1. Persons nominated and trained to use fire extinguishing appliances?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | ***Staff who will be attending this unit will have the necessary training - however it is made clear that a fire should only be tackled when in its early stages - their primary function is evacuation of occupants*** |
| 1. 25.6
 | 1. Persons nominated and trained to assist with evacuation, including evacuation of disabled people?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  |  |
| 1. 25.7
 | 1. Appropriate liaison with fire and rescue service (e.g. by fire and rescue service crews visiting for familiarization visits)?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | 1. ***The Fire Officer maintains good contact with Operational and fire safety staff in Dorset and Wiltshire Fire and Rescue Service.***
 |
| 1. 25.8
 | 1. Routine in‑house inspections of fire precautions (e.g. in the course of health and safety inspections)?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | 1. ***None***
 |

 |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |
| --- | --- |
| 1. **26.**
 | 1. **TRAINING AND DRILLS**
 |
| 1. 26.1
 | 1. Are all staff given adequate fire safety instruction and training on induction?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | 1. ***The initial induction training is given by line managers; additionally a bespoke fire safety on line package is used throughout the University, it is encouraged that new employees complete the module as soon as possible after they have started.***
 |
| 1. 26.2
 | 1. Are all staff given adequate periodic “refresher training” at suitable intervals?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | 1. ***The online training detailed above is completed annually by staff.***
 |
| 1. 26.3
 | 1. Does all staff training provide information, instruction or training on the following:
 |  |  |  |  |  |  |
|  | 1. N/A
 |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Fire risks in the premises?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. The fire safety measures in the building?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Action in the event of fire?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Action on hearing the fire alarm signal?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Method of operation of manual call points?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Location and use of fire extinguishers?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Means for summoning the fire and rescue service?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  | 1.
 |  |  |  |  |  |  |
|  | 1. Identity of persons nominated to assist with evacuation?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  | 1.
 |  |  |  |  |  |  |
|  | 1. Procedures for the safe evacuation of all occupants?
 |  |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | 1. ***The online package mentioned above covers all the issues detailed above.***
 |

 |  |
|  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1. 26.4
 | 1. Are staff with special responsibilities (e.g. fire wardens) given additional training?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | 1. ***Fire Wardens are given initial training and refresher training is provided every three years this includes fire extinguisher training. As the building is unoccupied no fire wardens will be present.***
 |
| 1. 26.5
 | 1. Are fire drills carried out at appropriate intervals?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  |  |
| 1. 26.6
 | 1. When the employees of another employer work in the premises:
 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Is their employer given appropriate information (e.g. on fire risks and general fire precautions)?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Is it ensured that the employees are provided with adequate instructions and information?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  | 1. Each member of staff
 |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |  |  |  |  |  |  |
|  | 1. ***Paperwork provided and induction package giving to external contractors on arrival at the Estates Office in Poole House prior to being allowed to undertake work for BU.***
 |
|  |  |  |  |  |  |  |  |
| 1. **27.**
 | 1. **TESTING AND MAINTENANCE**
 |
| 1. 27.1
 | 1. Adequate maintenance of premises?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments and deficiencies observed:
 |
|  | 1. ***Refer to comments below***
 |
| 1. 27.2
 | 1. Weekly testing and periodic servicing of fire detection and alarm system?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments and deficiencies observed:
 |
|  |  |
| 1. 27.3
 | 1. Monthly and annual testing routines for emergency escape lighting?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments and deficiencies observed:
 |
|  | 1. ***System serviced in accordance with BS5266 Pt 1***
2. ***Installation certificates confirming compliance should be available.***
 |
| 1. 27.4
 | 1. Routine inspection and annual maintenance
2. of fire extinguishers.
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments and deficiencies observed:
 |
|  | 1. ***Currently no P50 6 litre foam extinguisher installed in premises***
 |
| 1. 27.5
 | 1. Periodic inspection of external escape staircases, paths and gangways?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments and deficiencies observed:
 |
|  | 1. ***None***
 |
| 1. 27.6
 | 1. Six‑monthly inspection and annual testing of rising mains?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments and deficiencies observed:
 |
|  |  |
| 1. 27.7
 | 1. Weekly and monthly testing, six monthly inspection and annual testing of fire‑fighting lifts?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments and deficiencies observed:
 |
|  | 1. ***None***
 |
| 1. 27.8
 | 1. Weekly testing and periodic inspection of sprinkler installations?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  | 1. ***None***
 |

 |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1. 27.9
 | 1. Routine checks of final exit doors and/or securityfastenings?
 | 1. N/A
 |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  |  |  |  |  |  |  |
|  | 1. Comments:
2. ***Procedures being developed for this site.***
 |
| 1. 27.10
 | 1. Annual inspection and test of lightning protection system?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 |  | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
2. ***None***
 |
| 1. 27.11
 | 1. Routine inspection and testing of fire resisting doors?
 | 1. N/A
 | 1. **X**
 | 1. Yes
 | 1.
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Comments:
 |
|  |  |  | 1. **√**
 |  |  |  |  |
| 1. 27.12
 | 1. Other relevant inspections or tests:
 |
|  | 1. ***None***
 |
|  | 1. Comments:
 |
|  |  |
| 1. **28.**
 | 1. **RECORDS**
 |
| 1. 28.1
 | 1. Appropriate records of:
 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
|  | 1. Fire drills?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Fire training?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Fire alarm tests?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Emergency escape lighting tests?
 | 1. N/A
 |  | 1. Yes
 | 1. **X**
 | 1. No
 |  |
|  |  |  |  |  |  |  |  |
|  | 1. Maintenance and testing of other fire protection systems/provisions including sprinklers, portable fire fighting equipment, fire doors and exit doors.
 | 1. N/A
 |  | 1. Yes
 |  | 1. No
 | 1. **X**
 |
|  | 1.
 |  |  |  |  |  |  |
| 1. 28.2
 | 1. Comments:
 |
|  | 1. ***Central records are maintained***
2. ***Two water extinguishers on site that have not been tested***
 |

 |  |
|  |  |  |

|  |  |  |
| --- | --- | --- |
|  | 1. **FIRE RISK ASSESSMENT**
 |  |
|  |

|  |
| --- |
| 1. The following simple risk level estimator is based on a more general health and safety risk level estimator of the type contained in BS 8800:
 |
|  |

|  |  |  |  |
| --- | --- | --- | --- |
| 1. **Potential consequences of fire**
2. **Likelihood of fire**
 | 1. **Slight harm**
 | 1. **Moderate harm**
 | 1. **Extreme harm**
 |
| 1. **Low**
 | 1. Trivial risk
 | 1. Tolerable risk
 | 1. Moderate risk
 |
| 1. **Medium**
 | 1. Tolerable risk
 | 1. Moderate risk
 | 1. Substantial risk
 |
| 1. **High**
 | 1. Moderate risk
 | 1. Substantial risk
 | 1. Intolerable risk
 |

 |
| 1. Taking into account the fire prevention measures observed at the time of this risk assessment, it is considered that the hazard from fire (likelihood of fire) at these premises is:
 |
| 1. **Low**
 | 1. **X**
 | 1. **Medium**
 | 1.
 | 1. **High**
 |  |  |
|  |
| 1. In this context, a definition of the above terms is as follows:
 |
| **Low:** | 1. Unusually low likelihood of fire as a result of negligible potential sources of ignition.
 |
| 1. **Medium:**
 | 1. Normal fire hazards (e.g. potential ignition sources) for this type of occupancy, with fire hazards generally subject to appropriate controls (other than minor shortcomings).
 |
| **High:** | 1. Lack of adequate controls applied to one or more significant fire hazards, such as to result in significant increase in likelihood of fire.
 |
|  |
| 1. Taking into account the nature of the building and the occupants, as well as the fire protection and procedural arrangements observed at the time of this fire risk assessment, it is considered that the consequences for life safety in the event of fire would be:
 |
| 1. **Slight harm**
 | 1. **X X**
 | 1. **Moderate harm**
 | 1. **X**
 | 1. **Extreme harm**
 |  |  |
|  |
| 1. In this context, a definition of the above terms is as follows:
 |
| **Slight harm:** | 1. Outbreak of fire unlikely to result in serious injury or death of any occupant (other than an occupant sleeping in a room in which a fire occurs).
 |
| 1. **Moderate harm:**
 | 1. Outbreak of fire could foreseeably result in injury (including serious injury) of one or more occupants, but it is unlikely to involve multiple fatalities.
 |
| **Extreme harm:** | 1. Significant potential for serious injury or death of one or more occupants.
 |

 |  |
|  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |

|  |
| --- |
| 1. Accordingly, it is considered that the risk to life from fire at these premises is:
 |
| 1. **Trivial**
 | 1. **X**
 | 1. **Tolerable**
 | 1.
2.
 | 1. **Moderate**
 |  | 1. **Substantial**
 |  | 1. **Intolerable**
 |  |  |
|  |
| 1. Comments:
 |
| 1. ***None***
 |
| 1. A suitable risk‑based control plan should involve effort and urgency that is proportional to risk. The following risk‑based control plan is based on one advocated by BS 8800 for general health and safety risks:
 |
|

|  |  |
| --- | --- |
| 1. **Risk level**
 | 1. **Action and timescale**
 |
| 1. **Trivial**
 | 1. No action is required and no detailed records need be kept.
 |
| 1. **Tolerable**
 | 1. No major additional controls required. However, there might be a need for improvements that involve minor or limited cost.
 |
| 1. **Moderate**
 | 1. It is essential that efforts are made to reduce the risk. Risk reduction measures should be implemented within a defined time period.
2. Where moderate risk is associated with consequences that constitute extreme harm, further assessment might be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures.
 |
| 1. **Substantial**
 | 1. Considerable resources might have to be allocated to reduce the risk. If the building is unoccupied, it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken.
 |
| 1. **Intolerable**
 | 1. Building (or relevant area) should not be occupied until the risk is reduced.
 |

 |
|

|  |
| --- |
| 1. **(Note that, although the purpose of this section is to place the fire risk in context, the above approach to fire risk assessment is subjective and for guidance only. All hazards and deficiencies identified in this report should be addressed by implementing all recommendations contained in the following action plan. The fire risk assessment should be reviewed regularly.)**
 |

 |

 |  |
|  |  |  |
|  |  |  |